SECTION 26 0519 - LOW VOLTAGE POWER CONDUCTORS AND CABLES

1. GENERAL
   * + 1. RELATED DOCUMENTS
          1. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.
       2. SUMMARY
          1. This Section includes the following:

Building wires and cables rated 600 V and less.

Connectors, splices, and terminations rated 600 V and less.

Sleeves and sleeve seals for cables.

* + - * 1. Related Sections include the following:

Division 26 Section "Medium-Voltage Cables" for single-conductor and multiconductor cables, cable splices, and terminations for electrical distribution systems with 2001 to 35,000 V.

Division 26 Section "Undercarpet Electrical Power Cables" for flat cables for undercarpet installations.

Division 27 Section "Communications Horizontal Cabling" for cabling used for voice and data circuits.

* + - 1. DEFINITIONS
         1. EPDM: Ethylene-propylene-diene terpolymer rubber.
         2. NBR: Acrylonitrile-butadiene rubber.
      2. SUBMITTALS
         1. Product Data: For each type of product indicated.
         2. Qualification Data: For testing agency.
         3. Field quality-control test reports.
      3. QUALITY ASSURANCE
         1. Testing Agency Qualifications: An independent agency, with the experience and capability to conduct the testing indicated, that is a member company of the International Electrical Testing Association or is a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7, and that is acceptable to authorities having jurisdiction.

Testing Agency's Field Supervisor: Person currently certified by the International Electrical Testing Association or the National Institute for Certification in Engineering Technologies to supervise on-site testing specified in Part 3.

* + - * 1. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.
        2. Comply with NFPA 70.
      1. COORDINATION
         1. Set sleeves in cast-in-place concrete, masonry walls, and other structural components as they are constructed.

1. PRODUCTS
   * + 1. CONDUCTORS AND CABLES
          1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Alcan Products Corporation; Alcan Cable Division.

American Insulated Wire Corp.; a Leviton Company.

General Cable Corporation.

Cerro Wire & Cable Company.

Encore Wire Corporation.

Southwire Company.

Service Wire Co.

Phelps Dodge.

United Copper Industries.

Pyrotenax; Tyco products

AFC Cable; Tyco products

* + - * 1. Conductors: Comply with NEMA WC 70.

Copper: 98% conductivity copper; #12 AWG minimum; #10 AWG and smaller solid, #8 and larger stranded.

Aluminum: AA-8000 series alloy high conductivity, flexible, high torque retention, compact strand.

* + - * 1. Conductor Insulation: Comply with NEMA WC 70 for Types THHN-THWN.
        2. 2 Hour Fire Rated Cable Protective Assembly: type RHH UL 2196, UL 44 and F417 #25
        3. Multiconductor Cable: Comply with NEMA WC 70.

Health Care Grade Metal-clad cable, Type HCF-MC: UL Listed 1569 metal clad, galvanized steel or aluminum jacket applied over the inner cable assembly with spiral interlock armor and full-size insulated equipment grounding conductor in compliance with UL 1569 and NEC 330. Circuit assembly shall be cabled (twisted) with suitable lay length, and covered with durable polypropylene assembly tape.

* + - 1. CONNECTORS AND SPLICES
         1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
         2. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

AFC Cable Systems, Inc.

Bridgeport Fittings.

Hubbell Power Systems, Inc.

O-Z/Gedney; EGS Electrical Group LLC.

3M; Electrical Products Division.

Tyco Electronics Corp.

* + - * 1. Description: Factory-fabricated connectors and splices of size, ampacity rating, material, type, and class for application and service indicated.
      1. SLEEVES FOR CABLES
         1. Steel Pipe Sleeves: ASTM A 53/A 53M, Type E, Grade B, Schedule 40, galvanized steel, plain ends.
         2. Cast-Iron Pipe Sleeves: Cast or fabricated "wall pipe," equivalent to ductile-iron pressure pipe, with plain ends and integral waterstop, unless otherwise indicated.
         3. Sleeves for Rectangular Openings: Galvanized sheet steel with minimum 0.052- or 0.138-inch (1.3- or 3.5-mm) thickness as indicated and of length to suit application.
         4. Coordinate sleeve selection and application with selection and application of firestopping specified in Division 07 Section "Penetration Firestopping."
      2. SLEEVE SEALS
         1. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:
         2. Manufacturers: Subject to compliance with requirements, provide products by one of the following:
         3. Basis-of-Design Product: Subject to compliance with requirements, provide a comparable product by one of the following:

Advance Products & Systems, Inc.

Calpico, Inc.

Metraflex Co.

Pipeline Seal and Insulator, Inc.

* + - * 1. Description: Modular sealing device, designed for field assembly, to fill annular space between sleeve and cable.

Sealing Elements: EPDM interlocking links shaped to fit surface of cable or conduit. Include type and number required for material and size of raceway or cable.

Pressure Plates: Carbon steel. Include two for each sealing element.

Connecting Bolts and Nuts: Stainless steel of length required to secure pressure plates to sealing elements. Include one for each sealing element.

1. EXECUTION
   * + 1. CONDUCTOR MATERIAL APPLICATIONS
          1. Feeders: Copper for feeders smaller than No. 1 AWG; copper or aluminum for feeders No. 2 AWG and larger. Solid for No. 10 AWG and smaller; stranded for No. 8 AWG and larger.
          2. Branch Circuits: Copper. Solid for No. 10 AWG and smaller; stranded for No. 8 AWG and larger.
       2. CONDUCTOR INSULATION AND MULTICONDUCTOR CABLE APPLICATIONS AND WIRING METHODS
          1. Service Entrance: Type THHN-THWN, single conductors in raceway.
          2. Exposed Feeders: Type THHN-THWN, single conductors in raceway.
          3. Feeders Concealed in Ceilings, Walls, Partitions, and Crawlspaces: Type THHN-THWN, single conductors in raceway.
          4. Feeders Concealed in Concrete, below Slabs-on-Grade, and Underground: Type THHN-THWN, single conductors in raceway.
          5. Branch Circuits Concealed in Ceilings, Walls, and Partitions: Type THHN-THWN, single conductors in raceway, for Essential Systems; Metal-clad cable, Type HCF-MC, for normal systems.
          6. Branch Circuits Concealed in Concrete, below Slabs-on-Grade, and Underground: Type THHN-THWN, single conductors in raceway.
          7. Cord Drops and Portable Appliance Connections: Type SO, hard service cord with stainless-steel, wire-mesh, strain relief device at terminations to suit application.
          8. Class 1 Control Circuits: Type THHN-THWN, in raceway.
          9. Class 2 Control Circuits: Power-limited cable, concealed in building finishes.
          10. Wiring for controls and auxiliary systems #14 AWG stranded minimum with NEC type THWN insulation.
          11. Luminaire Wire: Incandescent - Use type SF-2, #16 for luminaires up to 300 watts, and #14 over 300 watts, except for luminaires in concrete pour use #12 or larger or as shown. Conductors in channels of, and flex to fluorescent luminaires type THHN or XHHW.
       3. INSTALLATION OF CONDUCTORS AND CABLES
          1. Connect circuits and feeders as shown on drawings. Drawings are diagrammatic and do not show every detail required in the wiring system. Detail wiring accomplished per NEC
          2. Conductors in parallel run feeders to be same size, same type, and same insulation, all cut same length. Bond each group of conductors making up a phase or neutral at both ends in an approved manner.
          3. Conceal cables in finished walls, ceilings, and floors, unless otherwise indicated.
          4. Use manufacturer-approved pulling compound or lubricant, Ideal "Yellow 77", Minerallac No. 100, or approved equal; compound used must not deteriorate conductor or insulation. Do not exceed manufacturer's recommended maximum pulling tensions and sidewall pressure values.

Do not use pulling compound for circuits on secondary side of ungrounded isolation transformers.

* + - * 1. Use pulling methods, including fish tape, cable, rope, and basket-weave wire/cable grips that will not damage cables or raceway.
        2. Install exposed cables parallel and perpendicular to surfaces of exposed structural members, and follow surface contours where possible.
        3. Support cables according to Division 26 Section "Hangers and Supports for Electrical Systems." Install wiring so conductors are not in tension or under excessive strain. Form wiring neatly and group in circuits. Tie grouped conductors with nylon ties, T&B "Tyrap" or approved equal.
        4. Support vertical conductor risers with non-conductive wedge support with conductor pre-drilled openings for the conductors. Provide conduit fitting and pullbox at each cable support location.
        5. Health Care Grade Multi-conductor MC cable:

Install Health Care Grade Multi-conductor MC cables only above accessible ceiling or in framed walls. Do not run in floor to floor penetrations. Homeruns from last outlet to area of the panel can be in flexible Healthcare MC conduit; No Health Care grade Multi-conductor MC cable may terminate at any panelboard. Transition to rigid conduit to terminate at the panelboard.

Installation shall be in accordance with applicable NEC Article. Support cable on 5-foot maximum intervals, and not more than 12-inches at box or cabinet. Support cables independent of suspended ceiling and ceiling support wires.

Cables shall be run perpendicular and parallel to the structure. Support groups of Healthcare MC cable with Eaton B-Line Series BRC5 or equal.

Fittings and connectors for Health Care Grade MC Cable shall be anti-short insulated bushing products specifically intended for Health Care Grade MC Cable.

Cut and strip cable with tools specifically intended for spiral-wound armored cable.

Health Care Grade MC Cable shall not be used for Essential System circuits in patient care areas.

* + - 1. IDENTIFICATION
         1. Identify and color-code conductors and cables according to Division 26 Section "Identification for Electrical Systems."
         2. Identify branch circuit number of conductors at panel terminations, including neutrals, with pre-printed adhesive labels.
         3. Securely fasten non-ferrous identifying tapes, pressure sensitive labels or engraved nameplates to all cables, feeders and power circuits in vaults, pull boxes, manholes, switchboard rooms, terminations of cables, etc.
         4. Color Code as follows and/or per local ordinances. Conductors #10 and smaller with colored insulation. Conductors #8 and larger not available in colors, color coded with colored pressure sensitive tape. Apply minimum 2" of tape to each individual [phase or neutral] conductor in half lapped pattern. [The equipment ground conductor shall be taped green for its entire exposed length.] Color-code as follows:

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Phase | 120/240 Volts | 120/208 Volts | 277/480 Volts | Ungrounded | Isolated Power  120/208 |
| A | Black | Black | Yellow | Orange | Black |
| B | Red | Red | Orange | Brown | Red |
| C | Orange | Blue | Brown | Yellow | Blue |
| Neutral | White | White | White | White | White |
| Eq Grnd | Green | Green | Green | Green | Green |
| Iso Grd |  |  |  |  | Green / Black Stripe |

* + - 1. CONNECTIONS
         1. Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values. If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.
         2. Provide lugs where not furnished as part of equipment -furnish as specified above, to connect all conductors.
         3. Furnish lugs for conductors #2/0 and larger with two bolt tongue or approved equivalent.
         4. Make splices and taps that are compatible with conductor material and that possess equivalent or better mechanical strength and insulation ratings than un-spliced conductors.

Taps in conductors # 8 and larger formed with a second conductor with bolted insulated connector, T&B "IDT", Ilsco "KUP-L-TAP" or approved equivalent. Insulate splices with 600 volt "heat shrink" covers by T&B or equal.

Splices in conductors # 8 and larger made with solid barrel-type fittings applied with an appropriate hydraulic tool. Splices used only where approved. Splice fittings: Burndy "Hydent". Insulate splices with 600 volt "heat shrink" covers T&B or equal.

Wire Joints with conductors #10 and smaller made with screw-on wire joints with insulating caps, installed with Tool or socket wrench;,.

Ideal Super/Nuts;

3M "Scotchlock"

Buchanan Electric Products B Cap

Where joints are made in damp or wet locations insulate splices with 600 volt “heat shrink” covers T&B or equal.

Apply oxide inhibitor in all splices and taps for aluminum conductors.

* + - * 1. Conductor Terminations:

Copper Conductors:

Lugs [in dry locations] connected to copper bus: 98% conductivity copper or bronze Thomas & Betts "Locktite", Burndy "QA" or approved equivalent.

[Lugs in ![damp locations] connected to copper bus: Solid 98% conductivity long copper barrel, tin plated, compression type connectors, Thomas & Betts color keyed, Burndy "Hydent" or approved equal; applied with appropriate hydraulic tool.]

Lugs in dry locations and lugs connected to aluminum bus - heavy casting aluminum, CU/AL rated, listed under UL Standard 486B, rated 90 degrees C; plated to prevent electrolysis, Thomas & Betts, Blackburn, and Ilsco or approved equivalent.

Aluminum Conductors:

Lugs connected to aluminum bus - heavy casting aluminum, CU/AL rated, listed under UL Standard 486B, rated 90 degrees C; plated to prevent electrolysis, Thomas & Betts, Blackburn, and Ilsco or approved equivalent.

Where conductors are connected to screw terminals, use nylon insulated locking fork, T&B Sta-Kon or approved equal.

* + - * 1. Wiring at Outlets: Install conductor at each outlet, with at least 12 inches of slack.
      1. SLEEVE INSTALLATION FOR ELECTRICAL PENETRATIONS
         1. Coordinate sleeve selection and application with selection and application of firestopping specified in Division 07 Section "Penetration Firestopping."
         2. Concrete Slabs and Walls: Install sleeves for penetrations unless core-drilled holes or formed openings are used. Install sleeves during erection of slabs and walls.
         3. Use pipe sleeves unless penetration arrangement requires rectangular sleeved opening.
         4. Rectangular Sleeve Minimum Metal Thickness:

For sleeve rectangle perimeter less than 50 inches (1270 mm) and no side greater than 16 inches (400 mm), thickness shall be 0.052 inch (1.3 mm).

For sleeve rectangle perimeter equal to, or greater than, 50 inches (1270 mm) and 1 or more sides equal to, or greater than, 16 inches (400 mm), thickness shall be 0.138 inch (3.5 mm).

* + - * 1. Fire-Rated Assemblies: Install sleeves for penetrations of fire-rated floor and wall assemblies unless openings compatible with firestop system used are fabricated during construction of floor or wall.
        2. Cut sleeves to length for mounting flush with both wall surfaces.
        3. Extend sleeves installed in floors 2 inches (50 mm) above finished floor level.
        4. Size pipe sleeves to provide 1/4-inch (6.4-mm) annular clear space between sleeve and cable unless sleeve seal is to be installed or unless seismic criteria require different clearance.
        5. Seal space outside of sleeves with grout for penetrations of concrete and masonry and with approved joint compound for gypsum board assemblies.
        6. Interior Penetrations of Non-Fire-Rated Walls and Floors: Seal annular space between sleeve and cable, using joint sealant appropriate for size, depth, and location of joint according to Division 07 Section "Joint Sealants."
        7. Fire-Rated-Assembly Penetrations: Maintain indicated fire rating of walls, partitions, ceilings, and floors at cable penetrations. Install sleeves and seal with firestop materials according to Division 07 Section "Penetration Firestopping."
        8. Roof-Penetration Sleeves: Seal penetration of individual cables with flexible boot-type flashing units applied in coordination with roofing work.
        9. Aboveground Exterior-Wall Penetrations: Seal penetrations using sleeves and mechanical sleeve seals. Size sleeves to allow for 1-inch (25-mm) annular clear space between pipe and sleeve for installing mechanical sleeve seals.
        10. Underground Exterior-Wall Penetrations: Install cast-iron "wall pipes" for sleeves. Size sleeves to allow for 1-inch (25-mm) annular clear space between cable and sleeve for installing mechanical sleeve seals.
      1. SLEEVE-SEAL INSTALLATION
         1. Install to seal underground exterior-wall penetrations.
         2. Use type and number of sealing elements recommended by manufacturer for cable material and size. Position cable in center of sleeve. Assemble mechanical sleeve seals and install in annular space between cable and sleeve. Tighten bolts against pressure plates that cause sealing elements to expand and make watertight seal.
      2. FIRESTOPPING
         1. Apply firestopping to electrical penetrations of fire-rated floor and wall assemblies to restore original fire-resistance rating of assembly according to Division 07 Section "Penetration Firestopping."
      3. FIELD QUALITY CONTROL
         1. Testing Agency: Engage a qualified testing agency to perform tests and inspections and prepare test reports.
         2. Perform tests and inspections and prepare test reports.
         3. Tests and Inspections:

After installing conductors and cables and before electrical circuitry has been energized, test service entrance and feeder conductors for compliance with requirements.

Perform each visual and mechanical inspection and electrical test stated in NETA Acceptance Testing Specification. Certify compliance with test parameters.

* + - * 1. Infrared Scanning: After Substantial Completion, but not more than 60 days after Final Acceptance, perform an infrared scan of each splice in cables and conductors No. 3 AWG and larger. Remove box and equipment covers so splices are accessible to portable scanner.

Follow-up Infrared Scanning: Perform an additional follow-up infrared scan of each splice 11 months after date of Substantial Completion.

Instrument: Use an infrared scanning device designed to measure temperature or to detect significant deviations from normal values. Provide calibration record for device.

Record of Infrared Scanning: Prepare a certified report that identifies splices checked and that describes scanning results. Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

* + - * 1. Test Reports: Prepare a written report to record the following:
        2. Test procedures used.
        3. Test results that comply with requirements.
        4. Test results that do not comply with requirements and corrective action taken to achieve compliance with requirements.
        5. Remove and replace malfunctioning units and retest as specified above.

END OF SECTION