SECTION 26 0923 - LIGHTING CONTROL DEVICES

PART 1 - GENERAL

1. RELATED DOCUMENTS
   1. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.
2. SUMMARY
   1. This Section includes the following lighting control devices:
      1. Time switches.
      2. Outdoor photoelectric switches.
      3. Switch-box occupancy sensors.
      4. Indoor occupancy sensors.
   2. Related Sections include the following:
      1. Electrical Division - Section "Switches and Receptacles" for manual light switches.
3. DEFINITIONS
   1. LED: Light-emitting diode.
   2. PIR: Passive infrared.
4. SUBMITTALS
   1. Product Data: For each type of product indicated.
   2. Shop Drawings: Show installation details for occupancy and light-level sensors.

PART 2 - PRODUCTS

1. GENERAL LIGHTING CONTROL DEVICE REQUIREMENTS
   1. Line-Voltage Surge Protection: An integral part of the devices for 120- and 277-V solid-state equipment. For devices without integral line-voltage surge protection, field-mounting surge protection shall comply with IEEE C62.41 and with UL 1449.
2. TIME SWITCHES
   1. Digital Time Switches: Electronic, solid-state programmable units with alphanumeric display complying with UL 917.
      1. Contact Configuration: SPDT (Single-Pole Double-Throw)
      2. Contact Rating: 20-A ballast load, 120/208/240/277 Vac. Contact output for both maintained and momentary (pulse) to allow control of latching contactors.
      3. Programs: 4 channels.
         1. For each channel, provide daily, weekly, or yearly schedules with a minimum of 1000 set points and an annual holiday schedule (up to 99 holidays) to override normal schedule.
      4. Circuitry: Allow connection of a photoelectric relay as substitute for on and off function of a program on selected channels.
      5. Astronomical Time: User scheduled for on or off function of a program on selected channels.
      6. Battery Backup: 8 year lithium battery.
      7. Memory: All programming and time functions shall be stored in EEPROM non-volatile memory.
      8. Surge Protection: Circuitry shall utilize transient voltage surge protection for voltage surges up to 6000V.
      9. Manual and Remote override.
      10. Approved Products: “Next Generation” series by Intermatic or equivalent by Tork.
   2. Wallbox Time Switch: Digital programmable time switch, designed to replace a standard toggle switch, to turn lights OFF after a preset time period.
      1. Completely self-contained control system, with standard single-gang switch device mounting and grounding strap with ground wire. Provide with compatible single-gang wallplate, color to match device (See section for “Switches and Receptacles” for device finish).
      2. Switching mechanism shall be a latching air gap relay and utilize “zero crossing circuitry” to maximize relay life. Switch shall also be capable of operating as a manual ON-OFF switch.
      3. Switch circuitry shall be compatible with all types of lighting loads, including tungsten, halogen, and fluorescent and HID ballasts (electro-magnetic and electronic).
      4. Switch shall have no minimum load requirement and be capable of handling up to 800 watts (at 120 volt) or 1200 watts (at 277 volt) of lighting load.
      5. Switch circuitry for time-off period shall be adjustable from 5 minutes to 12 hours (increments of 5 minutes up to one hour, and 15 minutes from 1 hour to 12 hours).
      6. The time switch shall have optional warnings, including light flash and audible beep, for notifying occupant that the time-off period is expiring.
      7. Approved Product: TS-400 by WattStopper, PTS 720 by Sensor Switch or TD200 by Hubbell.
3. OUTDOOR PHOTOELECTRIC SWITCHES
   1. Description: Solid state, with SPST dry contacts rated for 1800-VA tungsten or 1000-VA inductive, to operate connected relay, contactor coils, microprocessor input, and complying with UL 773A.
      1. Light-Level Monitoring Range: 1.5 to 10 fc (16 to 108 lx), with an adjustment for turn-on and turn-off levels within that range, and a directional lens in front of photocell to prevent fixed light sources from causing turn-off.
      2. Time Delay: 15-second minimum, to prevent false operation.
      3. Surge Protection: Metal-oxide varistor type, complying with IEEE C62.41 for Category A1 locations.
      4. Mounting: Twist lock complying with IEEE C136.10, with base-and-stem mounting or stem-and-swivel mounting accessories as required to direct sensor to the North sky exposure.
   2. Approved Product: K4000 series by Intermatic, or equal by Tork or Paragon.
4. INDOOR OCCUPANCY SENSORS
   1. Switch Box Sensors: PIR type with integral power-switching contacts rated for 800 W at 120-V ac, suitable for incandescent light fixtures, fluorescent light fixtures with magnetic or electronic ballasts, or 1/6-hp motors; (rated for 1000 W at 277-V ac).
      1. Approved product: Wattstopper PW-100, PW-200 or approved equal.
   2. Switch box sensors: Ultrasonic type with integral power-switching contacts rated for 800 W at 120-V ac, suitable for incandescent light fixtures, fluorescent light fixtures with magnetic or electronic ballasts, or 1/6-hp motors; (rated for 1000 W at 277-V ac).
      1. Approved product: Wattstopper UW-100 or approved equal.
   3. Wall- or ceiling-mounting, sensor.
      1. Operation: Unless otherwise indicated, turn lights on when covered area is occupied and off when unoccupied; with a time delay for turning lights off, adjustable over a minimum range of 1 to 30 minutes.
      2. Sensor Output: Contacts rated to operate the connected relay, complying with UL 773A. Sensor shall be powered from the relay unit. Sensor shall include auxiliary single-pole, double-throw isolated relay.
      3. Relay Unit: Dry contacts rated for 20-A ballast load at 120- and 277-V ac, for 13-A tungsten at 120-V ac, and for 1 hp at 120-V ac. Power supply to sensor shall be 24-V dc, 150-mA, Class 2 power source as defined by NFPA 70.
      4. Mounting:
         1. Sensor: Suitable for mounting in any position on a standard outlet box.
         2. Relay: Externally mounted though a 1/2-inch knockout in a standard electrical enclosure.
         3. Time-Delay and Sensitivity Adjustments: Recessed and concealed behind hinged door or coverplate.
      5. Indicator: LED, to show when motion is being detected during testing and normal operation of the sensor.
      6. Bypass Switch: Provide manual OFF/ON function facilitated by installation of a momentary contact switch.
         1. Approved Bypass Switch: Wattstopper LVS-1 or approved equal.
   4. PIR Type: Ceiling mounting; detect occupancy by sensing a combination of heat and movement in area of coverage.
      1. Detector Sensitivity: Detect occurrences of 6-inch minimum movement of any portion of a human body that presents a target of at least 36 sq. in..
      2. Detection Coverage (Room): Detect occupancy anywhere in a circular area of 1000 sq. ft. when mounted on a 96-inch- high ceiling.
      3. Detection Coverage (Corridor): Detect occupancy within 90 feet when mounted on a 10-foot- high ceiling.
      4. Approved Product: Wattstopper CX-105, CX-105-1, or CI-205-1.
   5. Ultrasonic Type: Ceiling mounting; detect occupancy by sensing a change in pattern of reflected ultrasonic energy in area of coverage.
      1. Detector Sensitivity: Detect a person of average size and weight moving at least 12 inches in either a horizontal or a vertical manner at an approximate speed of 12 inches/s.
      2. Detection Coverage (Small Room): Detect occupancy anywhere within a circular area of 600 sq. ft. when mounted on a 96-inch- high ceiling.
      3. Detection Coverage (Standard Room): Detect occupancy anywhere within a circular area of 1000 sq. ft. when mounted on an 8-foot- high ceiling.
      4. Detection Coverage (Large Room): Detect occupancy anywhere within a circular area of 2000 sq. ft. when mounted on a 96-inch- high ceiling.
      5. Detection Coverage (Corridor): Detect occupancy anywhere within 90 feet when mounted on a 10-foot- high ceiling in a corridor not wider than 14 feet.
      6. Approved Product: Wattstopper UT-305-3.
   6. Dual-Technology Type: Wall or Ceiling mounting; detect occupancy by using a combination of PIR and ultrasonic detection methods in area of coverage. Particular technology or combination of technologies that controls on and off functions shall be selectable in the field by operating controls on unit.
      1. Sensitivity Adjustment: Separate for each sensing technology.
      2. Detector Sensitivity: Detect occurrences of 6-inch minimum movement of any portion of a human body that presents a target of at least 36 sq. in., and detect a person of average size and weight moving at least 12 inches in either a horizontal or a vertical manner at an approximate speed of 12 inches/s.
      3. Detection Coverage (Standard Room): Detect occupancy anywhere within a circular area of 1000 sq. ft. when mounted on a 96-inch- high ceiling.
      4. Approved Product: Wattstopper DT-305 or DT-205.
   7. Approved Occupancy Sensor Manufacturers: Leviton, Hubbell, Novitas, Sensor Switch, or Wattstopper.
5. CONDUCTORS AND CABLES
   1. Power Wiring to Supply Side of Remote-Control Power Sources: Not smaller than No. 12 AWG.
   2. Classes 2 and 3 Control Cable: Multi-conductor cable with stranded copper conductors not smaller than No. 18 AWG.
   3. Class 1 Control Cable: Multi-conductor cable with stranded copper conductors not smaller than No. 14 AWG.
   4. Provide unshielded, twisted-pair cable for control and signal transmission conductors.

PART 3 - EXECUTION

1. SENSOR INSTALLATION
   1. Install according to manufacturer’s instructions. Install and aim sensors in locations to achieve at least 90 percent coverage of areas indicated. Do not exceed coverage limits specified in manufacturer's written instructions.
   2. Do not install ultrasonic or dual-technology occupancy sensors closer than 4 feet from air supply outlets/diffusers.
2. WIRING INSTALLATION
   1. Wiring Method: Comply with Division 26 Section "Conductors." Minimum conduit size shall be 1/2 inch.
   2. Wiring within Enclosures: Bundle, lace, and train conductors to terminal points. Separate power-limited and non-power-limited conductors according to conductor manufacturer's written instructions.
   3. Provide field-mounting transient voltage suppressors for lighting control devices locations that do not have integral line-voltage surge protection.
   4. Size conductors according to lighting control device manufacturer's written instructions, unless otherwise indicated.
   5. Splices, Taps, and Terminations: Make connections only on numbered terminal strips in junction, pull, and outlet boxes; terminal cabinets; and equipment enclosures.
   6. Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values. If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.
3. IDENTIFICATION
   1. Identify components and power and control wiring.
   2. Label time switches with a unique designation.
4. FIELD QUALITY CONTROL
   1. Perform the following field tests and inspections and prepare test reports:
      1. After installing time switches and sensors, and after electrical circuitry has been energized, adjust and test in compliance with manufacturer recommendations.
      2. Operational Test: Verify actuation of each sensor and adjust time delays per manufacturer’s instructions.
   2. Remove and replace lighting control devices where test results indicate that they do not function properly.
   3. Additional testing and inspecting, at Contractor's expense, may be performed to determine compliance of work with specified requirements.
5. ADJUSTING
   1. Occupancy Sensor Adjustments: When requested within 12 months of date of Substantial Completion, provide on-site assistance in adjusting sensors to suit actual occupied conditions. Provide up to two visits to site outside normal occupancy hours for this purpose.

END OF SECTION