SECTION 26 2816 - ENCLOSED SWITCHES AND CIRCUIT BREAKERS

PART 1- GENERAL

1. DESCRIPTION OF WORK:
2. Safety switches and disconnects and separately mounted circuit breakers.
3. Provide shop drawing.
4. RELATED WORK SPECIFIED ELSEWHERE:
5. FUSES
6. SUMMARY
7. This Section includes the following individually mounted, enclosed, switches and circuit breakers:
   * 1. Fusible switches.
        1. Non-fusible switches.
        2. Molded-case circuit breakers.
        3. Molded-case switches.
        4. Enclosures.
8. DEFINITIONS
   1. GD: General Duty
   2. GFCI: Ground-fault circuit interrupter
   3. HD: Heavy Duty
   4. RMS: Root mean square
   5. SPDT: Single pole, double throw
9. SUBMITTALS
10. Product Data: For each type of enclosed switch, circuit breaker, accessory, and component indicated. Include dimensioned elevations, sections, weights, and manufacturers’ technical data on features, performance, electrical characteristics, ratings, and finishes.
    * 1. Enclosure types and details for types other than NEMA 250, Type 1.
      2. Current and voltage ratings.
      3. Short-circuit current rating.
      4. UL Listing for series rating of installed devices.
      5. Features, characteristics, ratings, and factory settings of individual overcurrent protective devices and auxiliary components.
11. Shop Drawings: Diagram power, signal, and control wiring.
12. Operation and Maintenance Data: For enclosed switches and circuit breakers to include in emergency, operation, and maintenance manuals. In addition, include the following:
    * 1. Manufacturer’s written instructions for testing and adjusting enclosed switches and circuit breakers.
      2. Time-current curves, including selectable ranges for each type of circuit breaker.

PART 2 - PRODUCTS

1. FUSIBLE AND NON-FUSIBLE SWITCHES:
   1. Manufacturers:
      1. Eaton Corporation; Cutler-Hammer Products.
      2. General Electric Co.; Electrical Distribution & Control Division.
      3. Siemens Energy & Automation, Inc.
      4. Square D/Group Schneider.
   2. Fusible switch, NEMA KS 1, Type HD, with clips or bolt pads to accommodate specified fuses, lockable handle with capability to accept two padlocks, and interlocked with cover in closed position.
   3. Non-fusible switch, NEMA KS 1, Type HD, lockable handle with capability to accept two padlocks, and interlocked with cover in closed position.
   4. Accessories:
      1. Equipment Ground Kit: Internally mounted and labeled for copper and aluminum ground conductors.
      2. Neutral Kit: Internally mounted; insulated, capable of being grounded, and bonded; and labeled for copper and aluminum neutral conductors.
      3. Auxiliary Contact Kit: Auxiliary set of contacts arranged to open before switch blades open.
2. MOLDED-CASE CIRCUIT BREAKERS AND SWITCHES:
   1. Manufacturers:
      1. Eaton Corporation; Cutler-Hammer Products.
      2. General Electric Co.; Electrical Distribution & Control Division.
      3. Siemens Energy & Automation, Inc.
      4. Square D/Group Schneider.
   2. Molded-Case Circuit Breaker: NEMA AB 1, with interrupting capacity to meet available fault currents.
      1. Thermal-Magnetic Circuit Breakers: Inverse time-current element for low-level overloads and instantaneous magnetic trip element for short circuits. Adjustable magnetic trip setting for circuit-breaker frame sizes 150 A and larger.
      2. Adjustable Instantaneous-Trip Circuit Breakers: Magnetic trip element with front mounted, field adjustable trip setting.
      3. Electronic Trip-Unit Circuit Breakers: RMS sensing; field-replaceable rating plug; with the following field-adjustable settings:
         1. Instantaneous trip.
         2. Long- and short –time pickup levels.
         3. Long- and short –time adjustments.
         4. Ground-fault pickup level, time delay, and I2t response.
      4. Current-Limiting Circuit Breakers: Frame sizes 400 A and smaller and let-through ratings less than NEMA FU 1, RK-5.
      5. Integrally Fused Circuit Breakers: Thermal-magnetic trip element with integral limiter-style fuse listed for use with circuit breaker and trip activation on fuse opening or on opening of fuse compartment door.
      6. GFCI Circuit Breakers: Single- and two-pole configurations with 5 mA trip sensitivity.
   3. Molded-Case Circuit Breaker Feature and Accessories:
      1. Standard Frame sizes, trip ratings, and number of poles.
      2. Lugs: Mechanical style suitable for number, size, trip ratings, and conductor material.
      3. Application Listing: Type SWD for switching fluorescent lighting loads; Type HACR for heating, air-conditioning, and refrigerating equipment.
      4. Shunt Trip: 120-V trip coil energized from separate circuit, set to trip at 75 percent of rated voltage.
   4. Molded-Case Switches: Molded-case circuit breaker with fixed, high-set instantaneous trip only, and short-circuit withstand rating equal to equivalent breaker frame size interrupting rating.
   5. Molded-Case Switch Accessories:
      1. Verify that accessories retained below are available and appropriate for molded-case switch types and ratings retained.
      2. Lugs: Mechanical style suitable for number, size, trip ratings, and material of conductors.
      3. Application Listing: Type HACR for heating, air-conditioning, and refrigerating equipment.
      4. Shunt Trip: 120-V trip coil energized from separate circuit, set to trip at 75 percent of rated voltage. Provide "dummy" trip unit where required for proper operation.
3. ENCLOSURES
   1. NEMA AB 1 and NEMA KS 1 to meet environmental conditions of installed location.
      1. Outdoor Locations: NEMA 250, Type 3R.
      2. Other Wet or Damp Indoor Locations: NEMA 250, Type 4.

PART 3 - EXECUTION

1. EXAMINATION
   1. Examine elements and surfaces to receive enclosed switches and circuit breakers for compliance with installation tolerances and other conditions affecting performance.
   2. Proceed with installation only after unsatisfactory conditions have been corrected.
2. INSTALLATION
   1. Comply with applicable portions of NECA 1, NEMA PB 1.1, and NEMA PB 2.1 for installation of enclosed switches and circuit breakers.
   2. Mount individual wall-mounting switches and circuit breakers with tops at uniform height, unless otherwise indicated. Anchor floor-mounting switches to concrete base.
   3. Temporary Lifting Provisions: Remove temporary lifting eyes, channels, and brackets and temporary blocking of moving parts from enclosures and components.
3. IDENTIFICATION
   1. Identify field-installed conductors, interconnecting wiring, and components; provide warning signs as specified in Division 26 Section "Electrical Identification."
   2. Enclosure Nameplates: Label each enclosure with engraved metal or laminated-plastic nameplate as specified in Division 26 Section "Electrical Identification."
4. ADJUSTING
   1. Set field-adjustable switches and circuit-breaker trip ranges.
5. CLEANING
   1. On completion of installation, vacuum dirt and debris from interiors; do not use compressed air to assist in cleaning.
   2. Inspect exposed surfaces and repair damaged finishes.

END OF SECTION